| Application Reference: WA/108/24/PL Site Name: Stoneybrook Farm Eastergate Lane Walberton BN18 0BA |  |  |  | Initial Issue Date: 27/03/2025 Issue Date: Reviewer Reference: ADC/SB |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Summary and Recommendation: Objection Objection comments in bold, remaining comments to be addressed via condition. Please note: Any DOC application should only have a maximum of two consultation responses. If this is the second response for an open application and there are still comments outstanding, then please object to the application. |  |  |  |  |  |  |
|  | ADC Drainage Comments | Designer Response |  |  |  |  |
| Date: | 27/03/2025 | 31/03/25 |  |  |  |  |
| Condition Number: WA/108/24/PL |  |  |  |  |  |  |
| Comment Number |  |  |  |  |  |  |
|  | Please clarify the true bed level, top of bank level and existing connection level to the watercourse. | The bank level is 10.49m The inlet invert level set 1.102m below bank level = 9.388m Watercourse level set 9.350m |  |  |  |  |
|  | Please clarify the proposed connection level and demonstrate that a gravity connection can be achieved. This will include pipe gradients and invert levels at nodes. | Existing connection to be retained, proposed to connect into existing chamber by gravity. Hydraulic network calcs attached |  |  |  |  |
|  | Clarify any land raising that is proposed on the site and demonstrate that this will not increase flood risk. | The Exceedance Plan is attached, Surface Water routes to the existing low spots on the southern boundary. |  |  |  |  |
|  | Clearly show the location and easement for the watercourse on plans. | The watercourse easement is shown. |  |  |  |  |
|  | Site specific groundwater monitoring will be required. If infiltration is ruled out due to high groundwater levels and monitoring is abandoned, then groundwater must be assumed to be at ground level. |  |  |  |  |  |
|  | If groundwater levels allow then winter infiltration testing at the location, depth and head of water appropriate for the design must be completed. The testing depth must be at least 1m above the peak recorded groundwater level. |  |  |  |  |  |
|  | Ordinary watercourse land drainage consent or ADC Land Drainage Byelaw consent may be required. Evidence of this will need to be submitted. |  |  |  |  |  |
|  | Illustrate natural and exceedance flow paths on plans. |  |  |  |  |  |
|  | Submit an assessment of interception drainage and that surface water from the majority of frequent rainfall events will not leave the site. |  |  |  |  |  |
|  | Water quality assessment will need adjustment to reflect that the permeable paving does not serve all of the impermeable area and that the swale and detention basin are in fact one feature rather than acting in series. |  |  |  |  |  |
|  | Buoyancy calculations and a construction method statement relating to high groundwater may be required. |  |  |  |  |  |
|  | Contributing area plan must include the basin and the access road if this ultimately drains to this system. |  |  |  |  |  |
|  | Rainfall data must be adjusted to FEH22. |  |  |  |  |  |
|  | Please use the upper end climate change allowances correct at the time of determinations (currently 45% on the !% AEP event and 40% on the 3.33% AEP event). |  |  |  |  |  |
|  | A surcharged outfall will need to be modelled, this should be to the top of the bank where detailed watercourse modelling is not available. |  |  |  |  |  |
|  | Detailed plans and construction detail drawings will be required in accordance with the checklist. |  |  |  |  |  |
|  | If infiltration is not viable then the runoff rate is still subject to approval. |  |  |  |  |  |

If a designer would like a .docx version of this document to aid administration of responses, please request this by email to land.drainage@arun.gov.uk.